ENERGY AUDIT REPORT

ADVARIO SINGAPORE LIMITED

Submitted to

Advario Singapore Pte. Ltd.

21, Jurong Island Highway,

Singapore, 628208

NOVEMBER 2022

Submitted by

TÜV SÜD South Asia Pvt. Ltd.

G-11, Sector-11, Noida-201301

Uttar Pradesh, India

# ACKNOWLEDGEMENT

TÜV SÜD South Asia Pvt. Ltd, places on record its sincere thanks to Advario Singapore Limited for entrusting their confidence in TÜV SÜD South Asia for carrying out Energy Audit study at oil tanking terminal of Advario Singapore Limited – phase 6 & 10, for effective implementation of the Energy Conservation Measures (ECMs).

TÜV SÜD is grateful to Mr. Hendrick Ang from Advario Singapore Limited for their guidance and support.

We would also like to thank to Mr. Lennard Peh and Mr. Kapil Kharangate for their wholehearted support and cooperation extended by them during the field studies and preparation of the Energy Audit Report, without which the study would not have steered to its successful completion.

We are also thankful to the operators, technicians and other personnel for their continuous support and guidance in undertaking this exhaustive task of detailed energy audit. The field study would not have been completed on time without their interaction and timely support. We are grateful for their co-operation during the entire process.

TUV SUD South Asia Pvt. Ltd

# CONTENTS

ACKNOWLEDGEMENT	1

CONTENTS	2

1.	EXECUTIVE SUMMARY	6

2.	INTRODUCTION	7

2.1.	Background of the project	7

3.	STUDY TEAM	7

4.	METHODOLOGY ADOPTED FOR ENERGY AUDIT	7

4.1.	Task-I	8

4.2.	Task-II	8

4.3.	Task-III	8

5.	PROFILE OF ADVARIO SINGAPORE LIMITED	9

5.1.	Unit information	9

5.2.	Schematic layout of tankfarms and pumps	9

5.3.	Transfer pump details	12

6.	ENERGY CONSUMPTION ANALYSIS	15

6.1.	Electrical energy consumption pattern	15

6.1.1.	Electrical billing pattern - Phase 6	15

6.1.2.	Electrical billing pattern - Phase 10	17

6.2.	Rooftop solar photovoltaic power generation trend	19

6.3	Nitrogen consumption pattern	21

6.4	Water consumption pattern	22

7.	TRANSFER PUMP PERFORMANCE ASSESSMENT	24

7.1.	Pump performance assessment – single pump operation	24

7.2.	Pump performance assessment – parallel pump operation	30

7.3.	Pump performance assessment – single pump dosing operation	31

7.4.	Pump performance assessment – single pump stripping operation (tank to tank)	32

7.5.	Pump performance assessment – single pump operation (plant to plant)	34

8.	ENERGY CONSERVATION MEASURES	36

8.1.	ECM1: Reducing the pump suction head by keeping the suction valve in full open condition	36

8.2.	ECM2: Reducing the pump discharge head by keeping the discharge valve to optimum open condition	38

8.3.	ECM3: Operating the single pump (1000 m3/hr) upto 90% motor loading instead of operating 2 pumps in parallel	40

8.4.	ECM4: Replacing the pumps with matching duty point and BEP (best efficiency point)	42

8.5.	ECM5: Installing demand controller to restrict the demand below contract demand for Phase 6	43

8.6.	ECM6: Running the smaller capacity pump for dosing operation	45

9.	Other observations & suggestions	47

9.1.	Soft starter for pump motors	47

9.2.	Energy measurement and monitoring	47

9.3.	Benchmarking - Specific energy consumption (SEC) monitoring	48

9.4.	Motor operated valves for suction and discharge	48

9.5.	Energy efficient motor	49

REFERENCES	50

Table 1 Summary of energy conservation measures recommended	6

Table 2 Study team	7

Table 3 General information	9

Table 4 Storage tank details	10

Table 5 Transfer pump design details	12

Table 6 Electrical bill details – Phase 6 (Jan-21 to Oct-22)	15

Table 7 Electrical bill details – Phase 10 (Jan-21 to Oct-22)	17

Table 8 Solar power generation trend	19

Table 9 Pump performance assessment – single pump operation	24

Table 10 Maximum permissible current THD as per IEEE standard	29

Table 11 Maximum permissible voltage THD as per IEEE standard	30

Table 12 Pump performance assessment – parallel pump operation	30

Table 13 Pump performance assessment – single pump dosing operation	31

Table 14 Pump performance assessment – single pump stripping operation	32

Table 15 Pump performance assessment – single pump operation (plant to plant)	34

Table 16 Cost benefit analysis of reducing the pump suction head by keeping the suction valve in full open condition	37

Table 17 Cost benefit analysis of reducing the pump discharge head by keeping the discharge valve to optimum open condition	39

Table 18 Pump trial with various suction and discharge valve opening positions	40

Table 19 Cost benefit analysis of operating the single pump (1000 m3/hr) upto 90% motor loading instead of operating 2 pumps in parallel	41

Table 20 Cost benefit analysis of replacing the pumps with matching duty point and BEP (best efficiency point)	42

Table 21 Demand variation – Phase 6 (Jan-21 to Oct-22)	43

Table 22 Cost benefit analysis of installing demand controller to restrict the demand below contract demand for Phase 6	44

Table 23 Pump performance assessment – single pump dosing operation	45

Table 24 Cost benefit analysis of running the smaller capacity pump for dosing operation	46

Figure 1 Geographical location of the plant	9

Figure 2 Tankfarm 16 & 17 schematic layout	11

Figure 3 Tankfarm 18 & 19 schematic layout	11

Figure 4 Tankfarm 21 schematic layout	12

Figure 5 Total consumption – Phase 6	16

Figure 6 Demand variation – Phase 6	16

Figure 7 Reactive power trend – Phase 6	17

Figure 8 Total consumption – Phase 10	18

Figure 9 Demand variation – Phase 10	18

Figure 10 Reactive power trend – Phase 10	19

Figure 11 Phase 6 generated solar kWh	20

Figure 12 Phase 10 generated solar kWh	21

Figure 13 Solar generated kWh/kWp	21

Figure 14 Voltage profile of P1614	25

Figure 15 Voltage THD profile of P1614	25

Figure 16 Current THD profile of P1614	26

Figure 17 Power profile of P1614	26

Figure 18 Voltage profile of P1616	26

Figure 19 Voltage THD profile of P1616	27

Figure 20 Current THD profile of P1616	27

Figure 21 Power profile of P1616	27

Figure 22 Voltage profile of P1611	28

Figure 23 Voltage THD profile of P1611	28

Figure 24 Current THD profile of P1611	29

Figure 25 Power profile of P1611	29

Figure 26 Power profile of P1620 (stripping operation)	33

Figure 27 Voltage THD profile of P1620 (stripping operation)	33

Figure 28 Current THD profile of P1620 (stripping operation)	33

Figure 29 Power profile of P1620 (stripping operation)	34

Figure 30 Voltage profile of P1617	35

Figure 31 Voltage THD profile of P1617	35

Figure 32 Current THD profile of P1617	36

Figure 33 Power profile of P1617	36

Figure 34 Soft starter: Starting current and stress profile during starting	47

# EXECUTIVE SUMMARY

Based on the measurement and analysis carried out during the energy audit, the summary of results is provided in the table below:-

Table 1 Summary of energy conservation measures recommended

| Sr. No. | ECM Name | Estimated Annual Energy Savings (kWh) | Estimated Annual Savings (SGD) | Estimated Investment (SGD) | Simple Payback (Months) |
| --- | --- | --- | --- | --- | --- |
| 1 | Reducing the pump suction head by keeping the suction valve in full open condition. | 156,102 | 15,610 | - | Immediate |
| 2 | Reducing the pump discharge head by keeping the discharge valve to optimum open condition. | 208,135 | 20,814 | - | Immediate |
| 3 | Operating the single pump (1000 m3/hr) upto 90% motor loading instead of operating 2 pumps in parallel. | 50,009 | 5,001 | - | Immediate |
| 4 | Replacing the pumps with matching duty point and BEP (Best Efficiency Point) | 101,466 | 10,147 | 50,000 | 59 |
| 5 | Installing demand controller to restrict the demand below contract demand for Phase 6 | - | 1,183 | 2,000 | 21 |
| 6 | Running the smaller capacity pump for dosing operation | 6,868 | 687 | - | Immediate |
| Total |  | 522,580 | 53,400 | 52,000 | 12 |

# INTRODUCTION

# Background of the project

The project is to undertake Energy Audit of Advario Singapore Limited. The basic objective of the Energy Audit was to study the operations/performance of electrical energy intensive equipment/ systems for identification of potential areas wherein energy savings are practically feasible.

TUV SUD South Asia Pvt. Ltd., a leading certification, Inspections, Testing & Auditing company, with strong worldwide presence, is entrusted with the task of auditing the facility for energy audit. The facility underwent through comprehensive assessment to identify key potential energy saving areas.

With increasing awareness for energy optimization, fuel cost escalation and potential for energy savings, the management decided for the energy audit of their facility. TUV SUD South Asia Pvt. Ltd. was chosen and the team with energy experts conducted the field studies. A team of energy auditors from TUV SUD visited the facility and carried out this audit. This report details the observation & the findings and presents opportunity to Advario Singapore Limited to implement the potential energy conservation measures to reduce total energy consumption.

This energy audit report for Advario Singapore Limited presents the analysis of the data collected, observations made and field trials undertaken. It is governed by the objectives, scope of work and methodology discussed in ensuing paragraphs.

# STUDY TEAM

Details of the study team comprising of following team members are as mentioned below.

Table 2 Study team

| Sr. No. | Team Members |
| --- | --- |
| 1 | Mr. Ramesh Kumar |
| 2 | Mr. Joseph Xia |
| 3 | Mr. Chinmaykumar Dalal |
| 4 | Mr. Rameshwar Harne |
| 5 | Mr. Veeresh Tike |

# METHODOLOGY ADOPTED FOR ENERGY AUDIT

A detailed energy audit was conducted at Advario Singapore Limited in the month of November 2022. The energy audit team of TUV SUD South Asia Pvt. Ltd. comprised of BEE certified energy auditors and field specific expert. During the field visit and primary data collection, sophisticated handheld instruments were used to carry out measurements of parameters. Detailed investigation and measurements of electrical system such as operating load assessment, major equipment assessments were carried out with a view to reduce the energy consumption levels. The current electricity metering system in the facilities was also reviewed with a view to identify the possibilities for energy and cost improvements. Data collected from the energy audit study were compared with the design data, wherever available and extent of deviations was evaluated. Discussions were held with various technical and operating staffs to understand the system and its operations. The energy audit study mainly focused on the evaluation of operational efficiency/performance of installed equipment in the premise from the energy conservation point of view.

# Task-I

- Conduct kick-off meeting

- Visit to the site to ascertain the availability of data, measurements points and system complexity

- Meeting with concerned coordinator at site to brief them regarding the objective and scope of the project

- Collecting information regarding operating hours, location, map etc. for conducting audit smoothly.

- Assessment of data availability (electricity bills, etc.) and placing request for required data

- Finalization of support required from data collection like electricity bills copies etc.

# Task-II

Energy auditing instruments used during field visit are listed below.

- Digital 3 phase power analyzer: For electrical parameters (V, A, kW, kVA, kWh, PF, Hz)

- Single Phase Power Analyzer: For electrical parameters.

- Ultrasonic Water Flow Meter for Pump Flow measurement

Parallel activities of noting observations on the following:

- SLD (Site Layout Diagram)

- Operation & maintenance practices

- Instrumentation in place and

- Existing practices to monitor energy consumption

# Task-III

- Analysis of data collected from site performance assessment of the equipment

- Conceptualization and development of energy cost reduction projects with cost benefit analysis

- Review of energy efficiency monitoring and submission of energy audit report to Advario Singapore Limited for review and approval

# PROFILE OF ADVARIO SINGAPORE LIMITED

Advario is a leading partner in liquid storage logistics with a global network handling a broad range of products from chemicals, gases and fuels to new energy products. They have decades of experience, a future-focused, holistic approach and a truly ambitious ESG (Environment, Social and Governance) agenda. They operate a network of 13 terminals around the world.

The terminal on Jurong island in Singapore (phase 6 and 10) has 32 storage tanks of 5000-30,000 cbm capacity. The clean petroleum products, fuel oil and petrochemicals are handled for blending, barge loading & unloading, ship to ship transfer via shoreline, tank to tank transfer and vessel loading & unloading.

# Unit information

Table 3 General information

| Company Name | Advario Singapore Limited (Phase 6 and 10) |
| --- | --- |
| Address | 21, Jurong Island Highway, Singapore 628208 |
| GPS Co-ordinates | 1.289782973654451, 103.72305353946253 |
| Contact Person Mobile No. Email ID | Mr. Peh Wei De Lennard +65 90929298 lennard.peh@advario.com |
| TUV SUD South Asia (P) Limited | Mr. Chinmaykumar Dalal |

Figure 1 Geographical location of the plant

# Schematic layout of tankfarms and pumps

There are two phases namely ‘Phase 6’ and ‘Phase 10’ having 24 nos. storage tanks in tankfarm no. 16, 17, 18 & 19 (phase 6) and 8 nos. storage tanks in tankfarm no. 21 (phase 10).

The details of storage tanks for different tankfarms are tabulated below.

Table 4 Storage tank details

| Tank no. | Product | Capacity (m3) | Diameter (m) | Height (m) | Tankfarm |
| --- | --- | --- | --- | --- | --- |
| Phase 6 |  |  |  |  |  |
| T-1601 | White Oil | 20000 | 36 | 22 | TF16 |
| T-1602 | White Oil | 20000 | 36 | 22 | TF16 |
| T-1603 | White Oil | 20000 | 36 | 22 | TF16 |
| T-1604 | Mogas | 6000 | 20 | 22 | TF16 |
| T-1605 | Mogas | 6000 | 20 | 22 | TF16 |
| T-1606 | Mogas | 6000 | 20 | 22 | TF16 |
| T-1607 | Mogas | 14000 | 30 | 22 | TF16 |
| T-1608 | Mogas | 14000 | 30 | 22 | TF16 |
| T-1609 | Mogas | 14000 | 30 | 22 | TF16 |
| T-1701 | White Oil | 20000 | 36 | 22 | TF17 |
| T-1702 | White Oil | 20000 | 36 | 22 | TF17 |
| T-1703 | White Oil | 20000 | 36 | 22 | TF17 |
| T-1704 | White Oil | 20000 | 36 | 22 | TF17 |
| T-1705 | White Oil | 20000 | 36 | 22 | TF17 |
| T-1706 | White Oil | 20000 | 36 | 22 | TF17 |
| T-1801 | White Oil | 30000 | 43.8 | 22 | TF18 |
| T-1802 | White Oil | 30000 | 43.8 | 22 | TF18 |
| T-1803 | White Oil | 30000 | 43.8 | 22 | TF18 |
| T-1804 | White Oil | 30000 | 43.8 | 22 | TF18 |
| T-1901 | White Oil | 20000 | 36 | 22 | TF19 |
| T-1902 | White Oil | 20000 | 36 | 22 | TF19 |
| T-1903 | White Oil | 10000 | 26 | 22 | TF19 |
| T-1904 | White Oil | 10000 | 26 | 22 | TF19 |
| T-1905 | White Oil | 7500 | 22 | 22 | TF19 |
| Phase 10 |  |  |  |  |  |
| T-2101 | White Oil | 20000 | 36 | 22 | TF21 |
| T-2102 | White Oil | 20000 | 36 | 22 | TF21 |
| T-2103 | White Oil | 20000 | 36 | 22 | TF21 |
| T-2104 | White Oil | 20000 | 36 | 22 | TF21 |
| T-2105 | White Oil | 14000 | 30 | 22 | TF21 |
| T-2106 | White Oil | 14000 | 30 | 22 | TF21 |
| T-2107 | White Oil | 6000 | 20 | 22 | TF21 |
| T-2108 | White Oil | 6000 | 20 | 22 | TF21 |

Figure 2 Tankfarm 16 & 17 schematic layout

Figure 3 Tankfarm 18 & 19 schematic layout

Figure 4 Tankfarm 21 schematic layout

# Transfer pump details

The terminal is in the business of transferring the petroleum products depending upon various transfer services. The pumps are major electrical energy consumer for both phases followed by air conditioners and lighting system. However,  the electrical consumption of air conditioners and lighting system is very nominal in comparison to electrical energy consumption of pumps, so the main focus of the energy audit was on the assessment of pumping system and identification of energy conservation measures in pumping operation.

The design details of transfer pumps for both phases are tabulated below.

Table 5 Transfer pump design details

| Pump no. | Type | Make | Model no. | Rated flow (m3/hr) | Rated head (m) | Rated motor power (kW) |
| --- | --- | --- | --- | --- | --- | --- |
| Phase 6 – Tankfarm 16 & 17 |  |  |  |  |  |  |
| P1611 | Centrifugal | KSB | CPKN S2 250-500 | 1000 | 60 | 220 |
| P1612 | Centrifugal | KSB | CPKN S2 250-500 | 1000 | 60 | 220 |
| P1613 | Centrifugal | KSB | CPKN S2 250-500 | 1000 | 60 | 220 |
| P1614 | Centrifugal | KSB | CPKN S2 250-500 | 1000 | 60 | 220 |
| P1615 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P1616 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P1617 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P1618 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P1619 | Positive displacement | Bornemann | HC 232-70/2/N | 309 | 60 | 90 |
| P1620 | Positive displacement | Bornemann | HC 232-70/2/N | 309 | 60 | 90 |
| P1631 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 90 | 160 |
| P1632 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 90 | 160 |
| Phase 6 – Tankfarm 18 & 19 |  |  |  |  |  |  |
| P1831 | Centrifugal | KSB | CPKN S2 250-500 | 1000 | 60 | 220 |
| P1832 | Centrifugal | KSB | CPKN S2 250-500 | 1000 | 60 | 220 |
| P1833 | Centrifugal | KSB | CPKN S2 250-500 | 1000 | 60 | 220 |
| P1834 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P1835 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P1836 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P1837 | Positive displacement | Bornemann | HC 232-70/2/N | 309 | 60 | 90 |
| P1838 | Positive displacement | Bornemann | HC 232-70/2/N | 309 | 60 | 90 |
| Phase 10 – Tankfarm 21 |  |  |  |  |  |  |
| P2131 | Centrifugal | KSB | CPKN S2 250-500 | 1000 | 60 | 220 |
| P2132 | Centrifugal | KSB | CPKN S2 250-500 | 1000 | 60 | 220 |
| P2133 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P2134 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P2135 | Centrifugal | KSB | CPKN S2 200-500 | 500 | 60 | 132 |
| P2136 | Positive displacement | Bornemann | HC 232-70/2/N | 309 | 60 | 90 |
| P2137 | Positive displacement | Bornemann | HC 232-70/2/N | 309 | 60 | 90 |
| P2138 | Positive displacement | Bornemann | HC 232-70/2/N | 309 | 60 | 90 |

# ENERGY CONSUMPTION ANALYSIS

# Electrical energy consumption pattern

The plant uses electrical energy for all prime movers i.e. transfer pumps, air conditioners and illumination. The primary source of electrical power for the plant is from SP Group. The plant has diesel generator set to meet the demand of electricity in case of power failure or scheduled power cut from the grid.

The power is received at 22 kV and it is stepped down to 430 V through 3000 kVA * 2 nos. power transformers in phase 6 and 2000 kVA * 1 no. transformer in phase 10. The electrical details as recorded and produced to the Energy Audit team by the plant for last 22 months (Jan 21 – Oct 22) period are consolidated and summarized in this chapter.

Tariff structure: The plant has high tension power source and the electricity billing for high tension category is done on two-part tariff structure i.e. one part for contracted capacity (contract demand) and second part for actual energy drawn during billing cycle.

Demand charges: Demand charges are billed on the contract demand i.e. 850 kW and not on actual demand. Excess demand charges are applicable in case maximum demand surpasses the contract demand.

Reactive power: Reactive power is measured but is billed only when it exceeds 62% of total active power drawn.

The table below depicts the electrical consumption outline for the last year.

# Electrical billing pattern - Phase 6

Table 6 Electrical bill details – Phase 6 (Jan-21 to Oct-22)

| Month | Peak active power (kWh) | Off-peak active power (kWh) | Total active power (kWh) | Contract demand (kW) | Maximum demand (kVA) | Reactive power (kVArh) | 62% of kWh |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Jan-21 | 83,131 | 51,710 | 1,34,841 | 850 | 548 | 80,325 | 83,602 |
| Feb-21 | 85,594 | 53,375 | 1,38,969 | 850 | 860 | 81,308 | 86,161 |
| Mar-21 | 1,00,631 | 63,997 | 1,64,628 | 850 | 782 | 97,979 | 1,02,070 |
| Apr-21 | 98,501 | 61,136 | 1,59,637 | 850 | 903 | 94,005 | 98,975 |
| May-21 | 95,481 | 59,660 | 1,55,141 | 850 | 710 | 88,747 | 96,188 |
| Jun-21 | 87,559 | 48,133 | 1,35,692 | 850 | 806 | 76,059 | 84,129 |
| Jul-21 | 88,817 | 58,647 | 1,47,465 | 850 | 762 | 83,433 | 91,428 |
| Aug-21 | 64,869 | 47,217 | 1,12,085 | 850 | 510 | 60,104 | 69,493 |
| Sep-21 | 70,413 | 50,946 | 1,21,359 | 850 | 692 | 66,838 | 75,243 |
| Oct-21 | 1,04,172 | 66,332 | 1,70,504 | 850 | 918 | 98,587 | 1,05,712 |
| Nov-21 | 83,954 | 51,882 | 1,35,837 | 850 | 668 | 77,900 | 84,219 |
| Dec-21 | 97,297 | 60,515 | 1,57,812 | 850 | 754 | 92,955 | 97,843 |
| Jan-22 | 1,15,356 | 67,421 | 1,82,777 | 850 | 928 | 1,09,094 | 1,13,322 |
| Feb-22 | 92,575 | 55,907 | 1,48,482 | 850 | 964.5 | 86,797 | 92,059 |
| Mar-22 | 1,08,428 | 64,277 | 1,72,704 | 850 | 724 | 1,03,807 | 1,07,077 |
| Apr-22 | 90,357 | 60,264 | 1,50,621 | 850 | 735 | 90,556 | 93,385 |
| May-22 | 1,01,996 | 62,144 | 1,64,140 | 850 | 582 | 98,901 | 1,01,767 |
| Jun-22 | 1,08,387 | 63,649 | 1,72,036 | 850 | 651 | 1,05,947 | 1,06,662 |
| Jul-22 | 1,09,120 | 64,813 | 1,73,933 | 850 | 882 | 1,07,092 | 1,07,838 |
| Aug-22 | 1,01,592 | 59,774 | 1,61,365 | 850 | 854 | 98,762 | 1,00,047 |
| Sep-22 | 81,170 | 49,517 | 1,30,687 | 850 | 660 | 77,500 | 81,026 |
| Oct-22 | 93,395 | 55,728 | 1,49,123 | 850 | 648 | 90,050 | 92,456 |

Active power consumption trend:

Figure 5 Total consumption – Phase 6

The plant consumed approximately 1,44,500 kWh/month in year 2021 and 1,60,600 kWh/month in year 2022.

Demand variation:

Figure 6 Demand variation – Phase 6

The contract demand for the plant is 850 kW and maximum demand is ranging from 510 kVA to 964 kVA for past two years. It has surpassed the contract demand in seven months and plant has paid excess demand charges for those months.

Reactive power trend:

Figure 7 Reactive power trend – Phase 6

The reactive power consumed for phase 6 is nearing to 62% of kWh and will be billed if it surpasses the threshold.

# Electrical billing pattern - Phase 10

Table 7 Electrical bill details – Phase 10 (Jan-21 to Oct-22)

| Month | Peak active power (kWh) | Off-peak active power (kWh) | Total active power (kWh) | Contract demand (kW) | Maximum demand (kVA) | Reactive power (kVArh) | 62% of kWh |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Jan-21 | 40,094 | 16,099 | 56,192 | 850 | 578 | 14,192 | 34,839 |
| Feb-21 | 23,224 | 16,249 | 39,473 | 850 | 536 | 4,876 | 24,473 |
| Mar-21 | 21,501 | 13,730 | 35,231 | 850 | 490 | 4,203 | 21,843 |
| Apr-21 | 21,354 | 17,399 | 38,753 | 850 | 451 | 7,801 | 24,027 |
| May-21 | 43,921 | 22,596 | 66,517 | 850 | 580 | 15,778 | 41,241 |
| Jun-21 | 27,018 | 21,769 | 48,787 | 850 | 519 | 10,487 | 30,248 |
| Jul-21 | 16,355 | 12,613 | 28,968 | 850 | 507 | 3,254 | 17,960 |
| Aug-21 | 20,545 | 11,623 | 32,168 | 850 | 431 | 4,236 | 19,944 |
| Sep-21 | 29,380 | 15,334 | 44,714 | 850 | 608 | 11,668 | 27,723 |
| Oct-21 | 30,779 | 26,721 | 57,500 | 850 | 515 | 12,694 | 35,650 |
| Nov-21 | 19,716 | 15,105 | 34,821 | 850 | 449 | 5,698 | 21,589 |
| Dec-21 | 21,085 | 17,526 | 38,611 | 850 | 448 | 6,735 | 23,939 |
| Jan-22 | 44,944 | 17,317 | 62,261 | 850 | 628 | 16,912 | 38,602 |
| Feb-22 | 32,663 | 15,949 | 48,612 | 850 | 601 | 28,172 | 30,139 |
| Mar-22 | 29,153 | 18,770 | 47,923 | 850 | 570 | 31,235 | 29,712 |
| Apr-22 | 26,714 | 21,654 | 48,368 | 850 | 503 | 32,358 | 29,988 |
| May-22 | 32,644 | 26,892 | 59,536 | 850 | 653 | 40,108 | 36,912 |
| Jun-22 | 28,502 | 21,499 | 50,001 | 850 | 504 | 34,020 | 31,001 |
| Jul-22 | 38,065 | 20,872 | 58,937 | 850 | 514 | 39,252 | 36,541 |
| Aug-22 | 25,307 | 13,110 | 38,417 | 850 | 659 | 25,442 | 23,819 |
| Sep-22 | 12,061 | 11,465 | 23,526 | 850 | 372 | 16,234 | 14,586 |
| Oct-22 | 24,620 | 14,028 | 38,648 | 850 | 399 | 26,412 | 23,962 |

Active power consumption trend:

Figure 8 Total consumption – Phase 10

The plant consumed approximately 43,450 kWh/month in year 2021 and 47,600 kWh/month in year 2022.

Demand variation:

Figure 9 Demand variation – Phase 10

The contract demand for the plant is 850 kW and maximum demand is ranging from 372 kVA to 659 kVA for past two years.

Reactive power trend:

Figure 10 Reactive power trend – Phase 10

The reactive power consumed for phase 10 has surpassed the threshold of 62% of kWh and it is being billed for past  is nearing to 62% of kWh and will be billed for past 8 months.

# Rooftop solar photovoltaic power generation trend

The plant has renewable power source and has installed rooftop solar photovoltaic for renewable power generation. It is operated and maintained by the outsourced agency and the plant purchases power in cheaper rate from them. Phase 6 has 10.94 kWp and phase 10 has 17.01 kWp solar PV installed on substation rooftops. The details of power generation through solar PV are tabulated below.

Table 8 Solar power generation trend

| Date | Phase 6 generated kWh | Phase 6 kWh/kWp | Phase 10 generated kWh | Phase 10 kWh/kWp |
| --- | --- | --- | --- | --- |
| 01-Nov-22 | 27 | 2.47 | 40 | 2.35 |
| 02-Nov-22 | 24.43 | 2.23 | 38.11 | 2.24 |
| 03-Nov-22 | 20.1 | 1.84 | 30.72 | 1.81 |
| 04-Nov-22 | 49.36 | 4.51 | 79.48 | 4.67 |
| 05-Nov-22 | 12.72 | 1.16 | 20.08 | 1.18 |
| 06-Nov-22 | 41.53 | 3.80 | 60.89 | 3.58 |
| 07-Nov-22 | 48.04 | 4.39 | 73.86 | 4.34 |
| 08-Nov-22 | 37.38 | 3.42 | 55.33 | 3.25 |
| 09-Nov-22 | 31.87 | 2.91 | 47.77 | 2.81 |
| 10-Nov-22 | 30.36 | 2.78 | 46.18 | 2.71 |
| 11-Nov-22 | 38.83 | 3.55 | 60.08 | 3.53 |
| 12-Nov-22 | 19.56 | 1.79 | 27.55 | 1.62 |
| 13-Nov-22 | 29.19 | 2.67 | 39.72 | 2.34 |
| 14-Nov-22 | 38.85 | 3.55 | 59.98 | 3.53 |
| 15-Nov-22 | 51.11 | 4.67 | 77.38 | 4.55 |
| 16-Nov-22 | 48.06 | 4.39 | 70.31 | 4.13 |
| 17-Nov-22 | 40.39 | 3.69 | 62.78 | 3.69 |
| 18-Nov-22 | 44.3 | 4.05 | 65.14 | 3.83 |
| 19-Nov-22 | 13.42 | 1.23 | 21.09 | 1.24 |
| 20-Nov-22 | 37.78 | 3.45 | 53.6 | 3.15 |
| 21-Nov-22 | 59.83 | 5.47 | 89.14 | 5.24 |
| 22-Nov-22 | 59.12 | 5.40 | 87.95 | 5.17 |
| 23-Nov-22 | 20.86 | 1.91 | 32.89 | 1.93 |
| 24-Nov-22 | 51.58 | 4.71 | 79.03 | 4.65 |
| 25-Nov-22 | 37.05 | 3.39 | 58.77 | 3.46 |
| 26-Nov-22 | 30.12 | 2.75 | 45.94 | 2.70 |
| 27-Nov-22 | 16.94 | 1.55 | 27.15 | 1.60 |
| 28-Nov-22 | 38.01 | 3.47 | 52.8 | 3.10 |
| 29-Nov-22 | 36.05 | 3.30 | 50.55 | 2.97 |
| 30-Nov-22 | 39.22 | 3.59 | 55.53 | 3.26 |

Figure 11 Phase 6 generated solar kWh

Figure 12 Phase 10 generated solar kWh

Figure 13 Solar generated kWh/kWp

The unit generation ranges from 1 kWh to 5.5 kWh/kWp/day depending upon the irradiation level during that day. The difference between kWh/kWp/day for both the phases is not noticeable. It is advisable to monitor  kWh/kWp/day to compare both rooftop solar PVs and if there is any deviation, it can be rectified at an early stage.

# Nitrogen consumption pattern

The plant uses Nitrogen for headspace flushing of tanks and pipelines. The Nitrogen is not generated in the premises and instead it is outsourced. The consumption details are tabulated below.

Table 9 Nitrogen consumption details

| Date | Tier 1 consumption (NM3) | Tier 2 consumption (NM3) | Total consumption (NM3) |
| --- | --- | --- | --- |
| Jan-21 | 14,756 | 244 | 15,000 |
| Feb-21 | 14,481 | 519 | 15,000 |
| Mar-21 | 14,731 | 269 | 15,000 |
| Apr-21 | 14,563 | 437 | 15,000 |
| May-21 | 14,903 | 97 | 15,000 |
| Jun-21 | 13,887 | 3,072 | 16,959 |
| Jul-21 | 15,000 | - | 15,000 |
| Aug-21 | 14,783 | 217 | 15,000 |
| Sep-21 | 14,953 | 47 | 15,000 |
| Oct-21 | 16,208 | - | 16,208 |
| Nov-21 | 17,568 | 5,583 | 23,151 |
| Dec-21 | 19,296 | - | 19,296 |
| Jan-22 | 13,989 | 11 | 14,000 |
| Feb-22 | 13,893 | 107 | 14,000 |
| Mar-22 | 13,895 | 105 | 14,000 |
| Apr-22 | 14,261 | 2,775 | 17,036 |
| May-22 | 13,784 | 216 | 14,000 |
| Jun-22 | 12,640 | 3,488 | 16,128 |
| Jul-22 | 12,544 | 1,456 | 14,000 |
| Aug-22 | 9,906 | 4,095 | 14,001 |
| Sep-22 | 14,632 | 446 | 15,078 |
| Oct-22 | 14,000 | - | 14,000 |

Figure 14 Nitrogen consumption trend

# Water consumption pattern

The plant uses water mainly for drinking and cleaning purposes. The water consumption details are tabulated below.

Table 10 Water consumption details

| Date | Potable water consumption (m3) | Industrial water consumption (m3) | Total water consumption (m3) |
| --- | --- | --- | --- |
| Jan-21 | 140 | 345 | 485 |
| Feb-21 | 174 | 341 | 515 |
| Mar-21 | 142 | 310 | 452 |
| Apr-21 | 102 | 455 | 557 |
| May-21 | 124 | 456 | 580 |
| Jun-21 | 141 | 556 | 697 |
| Jul-21 | 130 | 324.5 | 454.5 |
| Aug-21 | 142.7 | 233 | 375.7 |
| Sep-21 | 132 | 458 | 590 |
| Oct-21 | 114 | 195 | 309 |
| Nov-21 | 133 | 105 | 238 |
| Dec-21 | 220 | 198 | 418 |
| Jan-22 | 186 | 159 | 345 |
| Feb-22 | 260 | 377 | 637 |
| Mar-22 | 198 | 238 | 436 |
| Apr-22 | 68.8 | 239 | 307.8 |
| May-22 | 157 | 277 | 434 |
| Jun-22 | 78 | 576.2 | 654.2 |
| Jul-22 | 116 | 343.1 | 459.1 |
| Aug-22 | 141 | -30 | 111 |
| Sep-22 | 135.2 | 163.9 | 299.1 |
| Oct-22 | 117 | 54 | 171 |

Figure 15 Water consumption trend

# TRANSFER PUMP PERFORMANCE ASSESSMENT

The performance of the pump was evaluated as a ratio of hydraulic power delivered by pump to shaft power to pump. The pump performance was computed by measuring,

- Actual flow delivered by pumps with help of ultrasonic flow meter or tank level method

- Actual power consumption of the pump motor

- Suction & discharge pressure for pumps and calculating the differential head

The pump efficiency is computed as,

Hydraulic power (Ph) = Q (m3 /s) x Total head, hd - hs (m) x ρ (kg/m3) x g (m/s2) / 1000

Where,

hd - discharge head

hs – suction head

ρ - density of the fluid

g – acceleration due to gravity

Pump shaft power = Electrical input power * Motor efficiency

pump efficiency = Hydraulic power / Pump shaft power

pump overall efficiency = Hydraulic power / Electrical input power

The transfer pump performance assessment was done for different operating conditions and the results are depicted below.

# Pump performance assessment – single pump operation

Table 11 Pump performance assessment – single pump operation

| Particular | Unit | Pump 1614 | Pump 1616 | Pump 1611 |
| --- | --- | --- | --- | --- |
| Transfer type | - | Loading to vessel | Loading to vessel | Loading to vessel |
| Operation condition | - | Single pump | Single pump | Single pump |
| Date | - | 29-Nov-2022 | 30-Nov-2022 | 30-Nov-2022 |
| Time | - | 15:00 hrs | 12:45 hrs | 13:00 hrs |
| Rated parameters |  |  |  |  |
| Pump type | - | Centrifugal | Centrifugal | Centrifugal |
| Rated flow | m3/hr | 1000 | 500 | 1000 |
| Rated head | m | 60 | 60 | 60 |
| Motor rating | kW | 220 | 132 | 220 |
| Measured parameters |  |  |  |  |
| Total suction head | m | 3 | 3 | 1 |
| Total discharge head | m | 42 | 30 | 40 |
| Density | kg/m3 | 728.1 | 742 | 742 |
| Average flow delivered | m3/hr | 839 | 750 | 1100 |
| Motor input power | kW | 130 | 102 | 165 |
| Performance evaluation |  |  |  |  |
| Total head developed | m | 39 | 27 | 39 |
| Head utilization | % | 65 | 45 | 65 |
| Flow utilization | % | 84 | 150 | 110 |
| Hydraulic power developed by pump | kW | 65 | 41 | 87 |
| Motor input power | kW | 130 | 102 | 165 |
| Calculated overall (pump set) efficiency | % | 49.9 | 40.1 | 52.6 |
| Rated motor efficiency | % | 90 | 90 | 90 |
| Calculated pump efficiency | % | 55.5 | 44.6 | 58.4 |
| Specific energy consumption | kW/m3 | 0.155 | 0.136 | 0.150 |

Power parameter profile of P1614:

Figure 16 Voltage profile of P1614

Figure 17 Voltage THD profile of P1614

Figure 18 Current THD profile of P1614

Figure 19 Power profile of P1614

Power parameter profile of P1616:

Figure 20 Voltage profile of P1616

Figure 21 Voltage THD profile of P1616

Figure 22 Current THD profile of P1616

Figure 23 Power profile of P1616

Power parameter profile of P1611:

Figure 24 Voltage profile of P1611

Figure 25 Voltage THD profile of P1611

Figure 26 Current THD profile of P1611

Figure 27 Power profile of P1611

Observation:

The pumps have lower efficiency as they are not running at best efficiency point (BEP) i.e. rated head and flow.

Power parameters: The voltage level ranges from 405V to 424V and the voltage & current THD is within acceptable limit.

Permissible limits for THD as per IEEE standards:

Table 12 Maximum permissible current THD as per IEEE standard

| Individual harmonic order (odd harmonics) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Isc/IL | <11 | 11≤h≤17 | 17≤h≤23 | 23≤h≤35 | 35≤h | TDD |
| <20 | 4 | 2 | 1.5 | 0.6 | 0.3 | 5 |
| 20<50 | 7 | 3.5 | 2.5 | 1 | 0.5 | 8 |
| 50<100 | 10 | 4.5 | 4 | 1.5 | 0.7 | 12 |
| 100<1000 | 12 | 5.5 | 5 | 2 | 1 | 15 |
| >1000 | 15 | 7 | 6 | 2.5 | 1.4 | 20 |

Where,

Isc = Maximum short circuit current at point of common coupling (PCC)

IL = Maximum demand load current at PCC

TDD = Total demand distortion

Even harmonics are limited to 25% of the odd harmonic limits above.

Table 13 Maximum permissible voltage THD as per IEEE standard

| Total harmonic distribution for different voltage levels in % |  |  |
| --- | --- | --- |
| Bus voltage at PCC | Individual voltage distortion (%) | Total voltage distortion (%) |
| 69kV and below | 3.0 | 5.0 |
| 60kV thru 161kV | 1.5 | 2.5 |
| 161kV above | 1.0 | 1.5 |

# Pump performance assessment – parallel pump operation

Table 14 Pump performance assessment – parallel pump operation

| Particular | Unit | Pump 1611 | Pump 1616 |
| --- | --- | --- | --- |
| Transfer type | - | Loading to vessel | Loading to vessel |
| Operation condition | - | // with P1616 | // with P1611 |
| Date | - | 30-Nov-2022 | 30-Nov-2022 |
| Time | - | 11:45 hrs | 12:15 hrs |
| Rated parameters |  |  |  |
| Pump type | - | Centrifugal | Centrifugal |
| Rated flow | m3/hr | 1000 | 500 |
| Rated head | m | 60 | 60 |
| Motor rating | kW | 220 | 132 |
| Measured parameters |  |  |  |
| Total suction head | m | 3 | 4 |
| Total discharge head | m | 45 | 40 |
| Density | kg/m3 | 742 | 742 |
| Average flow delivered | m3/hr | 1067 | 533 |
| Motor input power | kW | 161 | 96 |
| Performance evaluation |  |  |  |
| Total head developed | m | 42 | 36 |
| Head utilization | % | 70.00 | 60.00 |
| Flow utilization | % | 107 | 107 |
| Hydraulic power developed by pump | kW | 91 | 39 |
| Motor input power | kW | 161.06 | 96.00 |
| Calculated overall (pump set) efficiency | % | 56.2 | 40.4 |
| Rated motor efficiency | % | 90 | 90 |
| Calculated pump efficiency | % | 62.5 | 44.9 |
| Specific energy consumption | kW/m3 | 0.151 | 0.180 |

Observation:

The pumps have lower efficiency as they are not running at best efficiency point (BEP) i.e. rated head.

# Pump performance assessment – single pump dosing operation

Table 15 Pump performance assessment – single pump dosing operation

| Particular | Unit | Pump 1611 |
| --- | --- | --- |
| Transfer type | - | Loading to vessel |
| Operation condition | - | Single pump dosing |
| Date | - | 01-Dec-2022 |
| Time | - | 09:30 hrs |
| Rated parameters |  |  |
| Pump type | - | Centrifugal |
| Rated flow | m3/hr | 1000 |
| Rated head | m | 60 |
| Motor rating | kW | 220 |
| Measured parameters |  |  |
| Total suction head | m | 1 |
| Total discharge head | m | 63 |
| Density | kg/m3 | 763.1 |
| Average flow delivered | m3/hr | 250 |
| Motor input power | kW | 106 |
| Performance evaluation |  |  |
| Total head developed | m | 62 |
| Head utilization | % | 103.33 |
| Flow utilization | % | 25 |
| Hydraulic power developed by pump | kW | 32 |
| Motor input power | kW | 106.38 |
| Calculated overall (pump set) efficiency | % | 30.3 |
| Rated motor efficiency | % | 90 |
| Calculated pump efficiency | % | 33.7 |
| Specific energy consumption | kW/m3 | 0.426 |

Observation:

The pump has very low efficiency as it is throttled heavily and is being operated away from best efficiency point (BEP) i.e. rated head and flow.

# Pump performance assessment – single pump stripping operation (tank to tank)

Table 16 Pump performance assessment – single pump stripping operation

| Particular | Unit | Pump 1620 |
| --- | --- | --- |
| Transfer type | - | Tank to tank |
| Operation condition | - | Single pump stripping |
| Date | - | 01-Dec-2022 |
| Time | - | 10:15 hrs |
| Rated parameters |  |  |
| Pump type | - | Positive displacement |
| Rated flow | m3/hr | 300 |
| Rated head | m | 60 |
| Motor rating | kW | 90 |
| Measured parameters |  |  |
| Total suction head | m | 2 |
| Total discharge head | m | 10 |
| Density | kg/m3 | 752 |
| Average flow delivered | m3/hr | 201 |
| Motor input power | kW | 34 |
| Performance evaluation |  |  |
| Total head developed | m | 8 |
| Head utilization | % | 13.33 |
| Flow utilization | % | 67 |
| Hydraulic power developed by pump | kW | 3 |
| Motor input power | kW | 33.93 |
| Calculated overall (pump set) efficiency | % | 9.7 |
| Rated motor efficiency | % | 90 |
| Calculated pump efficiency | % | 10.8 |
| Specific energy consumption | kW/m3 | 0.169 |

Figure 28 Power profile of P1620 (stripping operation)

Figure 29 Voltage THD profile of P1620 (stripping operation)

Figure 30 Current THD profile of P1620 (stripping operation)

Figure 31 Power profile of P1620 (stripping operation)

Observation:

The pump has lower efficiency as it is not running at best efficiency point (BEP) i.e. rated head and flow.

# Pump performance assessment – single pump operation (plant to plant)

Table 17 Pump performance assessment – single pump operation (plant to plant)

| Particular | Unit | Pump 1617 |
| --- | --- | --- |
| Transfer type | - | Plant to plant |
| Operation condition | - | Single pump |
| Date | - | 01-Dec-2022 |
| Time | - | 13:00 hrs |
| Rated parameters |  |  |
| Pump type | - | Centrifugal |
| Rated flow | m3/hr | 500 |
| Rated head | m | 60 |
| Motor rating | kW | 132 |
| Measured parameters |  |  |
| Total suction head | m | 17 |
| Total discharge head | m | 42 |
| Density | kg/m3 | 683 |
| Average flow delivered | m3/hr | 473 |
| Motor input power | kW | 76 |
| Performance evaluation |  |  |
| Total head developed | m | 25 |
| Head utilization | % | 41.67 |
| Flow utilization | % | 95 |
| Hydraulic power developed by pump | kW | 22 |
| Motor input power | kW | 76.30 |
| Calculated overall (pump set) efficiency | % | 28.9 |
| Rated motor efficiency | % | 90 |
| Calculated pump efficiency | % | 32.1 |
| Specific energy consumption | kW/m3 | 0.161 |

Figure 32 Voltage profile of P1617

Figure 33 Voltage THD profile of P1617

Figure 34 Current THD profile of P1617

Figure 35 Power profile of P1617

Observation:

The pump has lower efficiency as it is not running at best efficiency point (BEP) i.e. rated head and flow.

# ENERGY CONSERVATION MEASURES

# ECM1: Reducing the pump suction head by keeping the suction valve in full open condition

Existing operating conditions:

During energy efficiency assessment, It was observed that the while operating the pumps, the suction valves are kept around 20% open only. Though the liquid height is sufficient in the tank, the suction pressure remains to minimum. If the valve is kept open the suction head may go up to 10 meter (upto static head available in the tank).

Recommendations:

Liquid entering the impeller eye turns and is split into separate streams by the leading edges of the impeller vanes, an action which locally drops the pressure below that in the inlet pipe to the pump.

If the incoming liquid is at a pressure with insufficient margin above its vapour pressure, then vapour cavities or bubbles appear along the impeller vanes just behind the inlet edges. This phenomenon is known as cavitation and has three undesirable effects:

- The collapsing cavitation bubbles can erode the vane surface, especially when pumping water-based liquids.

- Noise and vibration are increased, with possible shortened seal and bearing life.

- The cavity areas will initially partially choke the impeller passages and reduce the pump performance.

In extreme cases, total loss of pump developed head occurs. The value, by which the pressure in the pump suction exceeds the liquid vapour pressure, is expressed as a head of liquid and referred to as Net Positive Suction Head Available (NPSHA).

As the suction valve are throttled, it affects the NPSHA though there is positive head available in the tanks. Throttling causes the pressure drop which sometimes leads to the cavitation.  As the suction head is dropped, the workdone i.e. hydraulic power developed by pump is increased. This will lead to increase in specific power consumption.

Hence, It is recommended to keep the suction valve opens fully to use the available head in the tanks.

Cost benefit analysis:

Expected savings from reducing the pump suction head by keeping the suction valve in full open condition would result in a cost benefit of about 15,610 SGD per year. Estimated investment for implementation of this measure is nil, and hence payback will be immediate. The calculations leading to the cost benefit analysis is provided in table.

Table 18 Cost benefit analysis of reducing the pump suction head by keeping the suction valve in full open condition

| Parameter | Unit | Value |
| --- | --- | --- |
| Existing scenario |  |  |
| Total suction head | m | 3.0 |
| Total discharge head | M | 42.0 |
| Density | kg/m3 | 728.1 |
| Average flow delivered | m3/hr | 839.0 |
| Motor input power | kW | 130.0 |
| Overall Pump set efficiency | % | 49.9 |
| Annual energy consumption for pumping (considering 90% of annual energy consumption is by pumping system) | kWh/year | 2,029,320 |
| Cost of energy | SGD/kWh | 0.10 |
| Estimated Energy cost | SGD | 202,932 |
| Proposed scenario |  |  |
| Estimated suction head after removing the throttling (3 meter increase in positive suction head) | m | 6.0 |
| Estimated running power | kW | 120.0 |
| Estimated annual energy consumption | kWh/year | 1,873,218 |
| Estimated Energy cost | SGD | 187,322 |
| Saving (Energy & Cost) |  |  |
| Annual energy Saving | kWh/year | 156,102 |
| Annual Cost Saving | SGD | 15,610 |
| Investment required | SGD | - |
| Payback | months | - |

# ECM2: Reducing the pump discharge head by keeping the discharge valve to optimum open condition

Existing operating conditions:

During energy efficiency assessment, It was observed that the while operating the pumps, the delivery valves are kept around 20% open only. This is causing around 5 to 10 meter of additional head on the pump discharge. This flow control strategy is used to eliminate the motor tripping issue during start up. The motor connections are done using direct online starter.

Recommendations:

There are various strategies to control the pump flow and load during start up.

- By Varying the speed using the VFD

- Installing the soft starter which will the motor load during the start up

- Using the star delta starter

- Manually controlling the flow by throttling the discharge valve.

In the flow control by throttling the valve the pump runs continuously and a valve in the pump discharge line is opened or closed to adjust the flow to the required value.

With the valve fully open, the pump operates at "Flow 1". When the valve is partially closed it introduces an additional friction loss in the system, which is proportional to flow squared. The new system curve cuts the pump curve at "Flow 2", which is the new operating point. The head difference between the two curves is the pressure drop across the valve.

So when the discharge valve is throttled, energy is therefore wasted overcoming the resistance through the valve at all flow conditions. There is some reduction in pump power absorbed at the lower flow rate, but the flow multiplied by the head drop across the valve, is wasted energy. It should also be noted that, while the pump will accommodate changes in its operating point as far as it is able within its performance range, it can be forced to operate high on the curve, where its efficiency is low, and its reliability is affected.

Hence, It is suggested to operate the pump with the discharge valve in maximum open condition. The opening of the can be decided considering the 80% to 85% loading of the motor. Also to remove fully the throttling energy losses, it is suggested to install the soft starters for the motors.

Cost benefit analysis:

Expected savings from reducing the pump discharge head by keeping the discharge valve to optimum open condition would result in a cost benefit of about 20,814 SGD per year. Estimated investment for implementation of this measure is nil, and hence payback will be immediate. The calculations leading to the cost benefit analysis is provided in table.

Table 19 Cost benefit analysis of reducing the pump discharge head by keeping the discharge valve to optimum open condition

| Parameter | Unit | Value |
| --- | --- | --- |
| Existing scenario |  |  |
| Total suction head | m | 3.0 |
| Total discharge head | M | 42.0 |
| Density | kg/m3 | 728.1 |
| Average flow delivered | m3/hr | 839.0 |
| Motor input power | kW | 130.0 |
| Overall Pump set efficiency | % | 49.9 |
| Annual energy consumption for pumping (considering 90% of annual energy consumption is by pumping system) | kWh/year | 2,029,320 |
| Cost of energy | SGD/kWh | 0.10 |
| Estimated Energy cost | SGD | 202,932 |
| Proposed scenario |  |  |
| Estimated Discharge head after removing the throttling (5 meter reduction) | m | 38.0 |
| Estimated running power | kW | 116.7 |
| Estimated annual energy consumption | kWh/year | 1,821,185 |
| Estimated Energy cost | SGD | 182,118 |
| Saving (Energy & Cost) |  |  |
| Annual energy Saving | kWh/year | 208,135 |
| Annual Cost Saving | SGD | 20,814 |
| Investment required | SGD | - |
| Payback | months | - |

# ECM3: Operating the single pump (1000 m3/hr) upto 90% motor loading instead of operating 2 pumps in parallel

Existing operating conditions:

During energy efficiency assessment, It was observed that while operating the two pumps in parallel, the discharge pressure goes up to 45 meter. Suction valves of both the pumps are kept open to 20% so that input flow will be optimum for both the pumps. The specific power consumption is 0.151 kW/m3 whereas when only single pump is in operation, it is around 0.139 kW/m3.

Recommendations:

One of the methods of increasing the flow, particularly for systems where static head is a high proportion of the total, is to install two or more pumps to operate in parallel. Variation of flow rate is achieved by switching on and off additional pumps to meet demand.

The system curve is usually not affected by the number of pumps that are running. For a system with a combination of static and friction head loss, it can be seen, in Figure below, that the operating point of the pumps on their performance curves moves to a higher head and hence lower flow rate per pump, as more pumps are started. It is also apparent that the flow rate with two pumps running is not double that of a single pump. If the system head were only static, then flow rate would be proportional to the number of pumps operating.

A trial was conducted during the site visit with the pumps in parallel operation and single pump in operation.

Table 20 Pump trial with various suction and discharge valve opening positions

| Particular | Unit | Trial 1 | Trial 2 | Trial 3 | Trial 4 | Trial 5 |
| --- | --- | --- | --- | --- | --- | --- |
| Date: 30-Nov-2022 |  |  |  |  |  |  |
| Operation | - | // with P16 | Only P11 | Only P11 | Only P11 | Only P11 |
| Suction pressure | m | -3 | -3 | 1 | 1 | 1 |
| Discharge pressure | m | 45 | 45 | 40 | 35 | 45 |
| Suction valve opening | % | 20 | 20 | 40 | 50 | 50 |
| Discharge valve opening | % | 20 | 20 | 20 | 40 | 50 |
| Flow delivered | m3/hr | 1067 | 1019 | 1112 | 1300 | 1354 |
| Motor rated Power | kW | 220 | 220 | 220 | 220 | 220 |
| Motor power | kW | 161 | 141 | 152 | 162 | 169 |
| Motor % loading | % | 66 | 58 | 62 | 66 | 69 |
| Specific power consumption | kW/m3 | 0.151 | 0.139 | 0.137 | 0.125 | 0.125 |
| Reduction in SPC | % | - | 8.1 | 9.3 | 17.3 | 17.3 |

Hence, It is suggested to operate single pump to the maximum loading of the motor instead of operating two pumps in parallel (with partial loading). The second pump can be started in case the flow delivered is not sufficient by single pump.

Cost benefit analysis:

Expected savings from operating the single pump (1000 m3/hr) upto 90% motor loading instead of operating 2 pumps in parallel would result in a cost benefit of about 5,001 SGD per year. Estimated investment for implementation of this measure is nil, and hence payback will be immediate. The calculations leading to the cost benefit analysis is provided in table.

Table 21 Cost benefit analysis of operating the single pump (1000 m3/hr) upto 90% motor loading instead of operating 2 pumps in parallel

| Parameter | Unit | Value |
| --- | --- | --- |
| Existing scenario |  |  |
| Specific power consumption while 2 pumps in parallel operation (P1611 + P1616) | kW/m3 | 0.161 |
| Annual energy consumption for parallel pumping (considering 10% of annual pumping energy consumption) | kWh/year | 225,480 |
| Cost of energy | SGD/kWh | 0.10 |
| Estimated Energy cost | SGD | 22,548 |
| Proposed scenario |  |  |
| Specific power consumption while single pump in operation (P1611 + P1616) | m | 0.125 |
| Estimated annual energy consumption of single pump operation instead of parallel pumping (considering 10% of total pumping energy consumption) | kWh/year | 175,471 |
| Estimated Energy cost | SGD | 17,547 |
| Saving (Energy & Cost) |  |  |
| Annual energy Saving | kWh/year | 50,009 |
| Annual Cost Saving | SGD | 5,001 |
| Investment required | SGD | - |
| Payback | Months | - |

# ECM4: Replacing the pumps with matching duty point and BEP (best efficiency point)

Existing operating conditions:

During energy efficiency assessment, based on measurement data, most of the pumps are running at 35 meter to 40 meter while the rated head of pump is 60 meter. All the pumps are operating at right hand side of best efficiency point.

Recommendations:

Centrifugal pumps are characterized by the relationship between the flow rate (Q) they produce and the pressure (H) at which the flow is delivered. Pump efficiency varies with flow and pressure, and it is highest at one particular flow rate.

The best efficiency point (BEP) of a pump is the operating point, flow rate (capacity) and head where the pump offers the peak of efficiency. However, the importance of BEP is more than efficiency and best performance. This is the operating point where the possibility of energy waste and unwanted force, vibration, noises, etc., are at the lowest. Therefore, BEP is closely related to the highest theoretical reliability and lowest possible risk or maintenance

When a pump is operating at the far right side of BEP, this leads to high flow in liquid passages, which causes high velocities and turbulences. The passages were not designed for this high flow. Therefore, there are high losses, local turbulences and localized stall and blockage in bottlenecks.

The high momentum of main flow tends to follow the curvature of the pump parts as flow in some sections might be blocked or stalled. At higher flow rates (right side of BEP), a twin vortex structure may be formed downstream of the impeller passage. The recirculation and twin vortex structure are attributed to the increase of total pressure loss and energy waste. As a result, both efficiency and head would be low when operating at the far right side of BEP.

Hence, It is recommended to select the pumps with current duty point and corresponding best efficiency point pump.

Cost benefit analysis:

Expected savings from replacing the pumps with matching duty point and BEP (best efficiency point) would result in a cost benefit of about 10,147 SGD per year. Estimated investment for implementation of this measure is 50,000 SGD, and hence payback will be 59 months. The calculations leading to the cost benefit analysis is provided in table.

Table 22 Cost benefit analysis of replacing the pumps with matching duty point and BEP (best efficiency point)

| Parameter | Unit | Value |
| --- | --- | --- |
| Existing scenario |  |  |
| Existing pump efficiency | % | 53.0 |
| Annual energy consumption for pumping (considering 90% of annual energy consumption is by pumping system) | kWh/year | 2,029,320 |
| Cost of energy | SGD/kWh | 0.10 |
| Estimated Energy cost | SGD | 202,932 |
| Proposed scenario |  |  |
| Estimated rise in pump efficiency when operating close to BEP | % | 5.0 |
| Estimated annual energy consumption | kWh/year | 1,927,854 |
| Estimated Energy cost | SGD | 192,785 |
| Saving (Energy & Cost) |  |  |
| Annual energy Saving | kWh/year | 101,466 |
| Annual Cost Saving | SGD | 10,147 |
| Investment required | SGD | 50,000 |
| Payback | Months | 59 |

# ECM5: Installing demand controller to restrict the demand below contract demand for Phase 6

Existing operating conditions:

During energy efficiency assessment, it was observed that in 7 months the maximum demand has surpassed contract demand (850 kW).

Table 23 Demand variation – Phase 6 (Jan-21 to Oct-22)

| Month | Contract demand (kW) | Maximum demand (kVA) | Excess demand (kVA) |
| --- | --- | --- | --- |
| Jan-21 | 850 | 548 | 0 |
| Feb-21 | 850 | 860 | 10 |
| Mar-21 | 850 | 782 | 0 |
| Apr-21 | 850 | 903 | 53 |
| May-21 | 850 | 710 | 0 |
| Jun-21 | 850 | 806 | 0 |
| Jul-21 | 850 | 762 | 0 |
| Aug-21 | 850 | 510 | 0 |
| Sep-21 | 850 | 692 | 0 |
| Oct-21 | 850 | 918 | 68 |
| Nov-21 | 850 | 668 | 0 |
| Dec-21 | 850 | 754 | 0 |
| Jan-22 | 850 | 928 | 78 |
| Feb-22 | 850 | 964.5 | 114.5 |
| Mar-22 | 850 | 724 | 0 |
| Apr-22 | 850 | 735 | 0 |
| May-22 | 850 | 582 | 0 |
| Jun-22 | 850 | 651 | 0 |
| Jul-22 | 850 | 882 | 32 |
| Aug-22 | 850 | 854 | 4 |
| Sep-22 | 850 | 660 | 0 |
| Oct-22 | 850 | 648 | 0 |

Recommendations:

The definition of contract demand is "the demand in Kilowatt (KW) or Kilo-volt Ampere (KVA) mutually agreed between the utility and the consumer as entered into the agreement or agreed through other written communication." Hence, contract demand means demand in Kilowatt (KW)/ Kilo-volt Ampere (KVA) mutually agreed between the electricity supplier and the consumer as entered into in the agreement or agreed through other written communication.

In the two-part energy tariff pattern, the facility pays for demand charges as well as energy charges. With due consideration to this demand data (actual maximum demand) and the type of load and operating time, it can be concluded that the facility can restrict the billed demand to 850 kW and get financial benefit due to reduction of excess demand charges as per norms of utility. It is important to note that while maximum demand is recorded, it is not the instantaneous demand drawn, as is often misunderstood, but the time integrated demand over the predefined recording cycle.

Following approach can be adapted to reduce the billed MD:

- Shedding of Non-Essential Loads: When the maximum demand tends to reach preset limit i.e. (in this case 850 kW), shedding some of non-essential loads temporarily can help to reduce it. It is possible to install direct demand monitoring systems, which will switch off non-essential loads when a preset demand is reached. Simple systems give an alarm, and the loads are shed manually. Sophisticated microprocessor-controlled systems are also available, which provide a wide variety of control options like:

- Accurate prediction of demand

- Graphical display of present load, available load, demand limit

- Visual and audible alarm

- Recording and metering

Hence it is suggested to install the maximum demand controller and monitor the maximum demand from utility meter on daily basis. This will help to understand when the demand goes to peak. Based on this appropriate action can be proposed to control the maximum demand. The APFC can also set to optimum valve (0.95) which will help to reduce the maximum demand.

Cost benefit analysis:

Expected savings from installing demand controller to restrict the demand below contract demand for Phase 6 would result in a cost benefit of about 1,143 SGD per year. Estimated investment for implementation of this measure is 2,000 SGD, and hence payback will be 21 months. The calculations leading to the cost benefit analysis is provided in table.

Table 24 Cost benefit analysis of installing demand controller to restrict the demand below contract demand for Phase 6

| Parameter | Unit | Value |
| --- | --- | --- |
| Existing scenario |  |  |
| Excess demand kVA for (Nov-21 to Oct-22) | kVA | 229 |
| Cost of excess demand charge | SGD/kVA | 5 |
| Excess demand charges | SGD | 2,285 |
| Proposed scenario |  |  |
| Proposed excess demand | kVA | - |
| Cost of excess demand charge | SGD/kVA | 5 |
| Excess demand charges | SGD | - |
| Saving (Energy & Cost) |  |  |
| Annual energy Saving | kWh/year | - |
| Annual Cost Saving | SGD | 1,143 |
| Investment required | SGD | 2,000 |
| Payback | Months | 21 |

# ECM6: Running the smaller capacity pump for dosing operation

Existing operating conditions:

During energy efficiency assessment, It was observed that the while dosing operation 1000 m3/hr flow rate pump was used and flow was throttled to 250 m3/hr through the discharge valve. The specific power consumption was 0.426 kW/m3.

Table 25 Pump performance assessment – single pump dosing operation

| Particular | Unit | Pump 1611 |
| --- | --- | --- |
| Transfer type | - | Loading to vessel |
| Operation condition | - | Single pump dosing |
| Date | - | 01-Dec-2022 |
| Time | - | 09:30 hrs |
| Rated parameters |  |  |
| Pump type | - | Centrifugal |
| Rated flow | m3/hr | 1000 |
| Rated head | m | 60 |
| Motor rating | kW | 220 |
| Measured parameters |  |  |
| Total suction head | m | 1 |
| Total discharge head | m | 63 |
| Density | kg/m3 | 763.1 |
| Average flow delivered | m3/hr | 250 |
| Motor input power | kW | 106 |
| Performance evaluation |  |  |
| Total head developed | m | 62 |
| Head utilization | % | 103.33 |
| Flow utilization | % | 25 |
| Hydraulic power developed by pump | kW | 32 |
| Motor input power | kW | 106.38 |
| Calculated overall (pump set) efficiency | % | 30.3 |
| Rated motor efficiency | % | 90 |
| Calculated pump efficiency | % | 33.7 |
| Specific energy consumption | kW/m3 | 0.426 |

Recommendations:

As explained in ECM2, controlling the flow by throttling the discharge valve leads to significant energy loss.

Hence, It is recommended to use the smaller capacity pump which is closer to the dosing flow requirement.

Cost benefit analysis:

Expected savings from running the smaller capacity pump for dosing operation would result in a cost benefit of about 687 SGD per year. Estimated investment for implementation of this measure is nil, and hence payback will be immediate. The calculations leading to the cost benefit analysis is provided in table.

Table 26 Cost benefit analysis of running the smaller capacity pump for dosing operation

| Parameter | Unit | Value |
| --- | --- | --- |
| Existing scenario |  |  |
| Specific power consumption while dosing (P1611) | kW/m3 | 0.426 |
| Running power of pump | kW | 106 |
| Estimated pump running hours | Hours/year | 100 |
| Annual energy consumption for dosing operation | kWh/year | 10,600 |
| Cost of energy | SGD/kWh | 0.10 |
| Estimated Energy cost | SGD | 1,060 |
| Proposed scenario |  |  |
| Specific power consumption while dosing by using smaller capacity pump | kW/m3 | 0.150 |
| Running power of pump | kW | 37 |
| Annual energy consumption for dosing operation | kWh/year | 3,732 |
| Estimated Energy cost | SGD | 373 |
| Saving (Energy & Cost) |  |  |
| Annual energy Saving | kWh/year | 6,868 |
| Annual Cost Saving | SGD | 687 |
| Investment required | SGD | - |
| Payback | Months | - |

# Other observations & suggestions

# Soft starter for pump motors

All the transfer pump motors have direct online starters. When starting, AC Induction motor develops more torque than is required at full speed. This stress is transferred to the mechanical transmission system resulting in excessive wear and premature failure. Additionally, rapid acceleration also has a massive impact on electricity supply charges with high inrush currents drawing +600% of the normal run current.

The use of Star Delta only provides a partial solution to the problem. Should the motor slow down during the transition period, the high peaks can be repeated and can even exceed direct on line current.

Figure 36 Soft starter: Starting current and stress profile during starting

Soft starter (see figure) provides a reliable and economical solution to these problems by delivering a controlled release of power to the motor, thereby providing smooth, stepless acceleration and deceleration. Motor life will be extended as damage to windings and bearings is reduced.

Soft Start & Soft Stop is built into 3 phase units, providing controlled starting and stopping with a selection of ramp times and current limit settings to suit all applications (see figure).

Advantages of Soft start,

- Less mechanical stress

- Improved power factor

- Lower maximum demand.

- Less mechanical maintenance

# Energy measurement and monitoring

For optimum use of energy, the energy consumption should be measured and monitored regularly. It is suggested to install cloud based submeters to major pumps and record and analyze data on daily basis. This data to be verified and analyzed regularly by authorized person so that any deviation can be rectified at an early stage.

# Benchmarking - Specific energy consumption (SEC) monitoring

Benchmarking is useful tool for understanding energy consumption patterns for taking measures to improve energy efficiency. It forms basis the basis for monitoring and target setting.

Energy benchmarking is a process in which the energy performance is of the plant is compared against a common metric that represents ‘standard’ or ‘optimal’ performance. Benchmarking energy performance permits:

- Quantification of energy consumption trends vis-à-vis pumping quantity

- Comparison of the industry energy performance with respect to various operating  levels (capacity utilization)

- Scope and margin available for energy consumption and cost reduction

- Basis for monitoring and target setting exercises

The specific energy consumption is energy used per output production i.e. kWh/m3 of fluid pumped or kWh/kg of fluid pumped. It is an important indicator of plant performance in terms of energy usage.

Presently, the plant does not monitor SEC as the workflow is not standard. The pumping operation is dependent upon the client requirement and preparing monthly/weekly schedules for pumping is bit challenging. However, energy consumption can be monitored with respect to the amount of fluid pumped and it will be useful to compare specific energy consumption with various operating conditions.

# Motor operated valves for suction and discharge

The plant has manual gate valves for suction and discharge pipeline of transfer pumps. The pump, tank and pipeline combination is changed as per client requirement and the suction & discharge valves need to be opened and closed frequently. Due to frequently opening and closing of valves, the operator tends to open the valves partially which affects the pump performance.

The motor operated valves (MOV) are very useful in case of frequent operation and if valves are located at remote or hazardous place. The valves can be operated by the operator from DCS depending upon the requirement. It is suggested to explore the possibility of changing frequently operated valves to MOV in phased manner.

# Energy efficient motor

Energy-efficient motors (EEM) are the ones in which, design improvements are incorporated specifically to increase operating efficiency over motors of standard design improvements focus on reducing intrinsic motor losses. Improvements include the use of lower-loss silicon steel, a longer core (to increase active material), thicker wires (to reduce resistance), thinner laminations, smaller air gap between stator and rotor, copper instead of aluminium bars in the rotor, superior bearings and a smaller fan, etc.

Energy-efficient motors operate with efficiencies that are typically 3 to 4 percentage points higher than standard motors. In keeping with the stipulations of the BIS, energy efficient motors are designed to operate without loss in efficiency at loads between 75 % and 100 % of rated capacity. This may result in major benefits in varying load applications. The power factor is about the same or may be higher than for standard motors. Furthermore, energy efficient motors have lower operating temperatures and noise levels, greater ability to accelerate higher-inertia loads, and are less affected by supply voltage fluctuations.

It is suggested to replace the motors that are old, rewound and continuously running with energy efficient motors.

# REFERENCES

- General aspects of Energy Management and Energy Audit, Bureau of Energy Efficiency India

- Energy efficiency in thermal utilities, Bureau of Energy Efficiency India

- Energy efficiency in electrical utilities, Bureau of Energy Efficiency

- Energy performance assessment for equipment and utility system, Bureau of Energy Efficiency

- Energy audit manual (The practitioner’s guide), National Productivity Council

- Guide book Refresher course for Energy Managers and Auditors, Bureau of Energy Efficiency India

- Manner and conduct of energy audit, Bureau of Energy Efficiency India

Ref: Electrical system, Energy efficiency in electrical utilities, book 3, Bureau of Energy Efficiency India